{"text_format":"1","workbook":"xlsx","n_sheets":15,"sheets":["Data","Perm Flow ","Feed Pres","Perm Con.","Salt Passage (Norm)","Perm Flow (Norm)","Differential Pres (Norm)","Water Trans. Coefficient","Salt Trans. Coefficient","Language","Data Collection Form","Cleaning Chem Use","Cleaning Data","Additional Data","Element Info"],"not_rendered":{"charts":16,"images":7,"macros":1,"external_links":2,"defined_names":210,"comments":1,"pivot_tables":0},"unopened":[{"sheet":"Perm Flow ","index":1,"reason":"not_a_worksheet"},{"sheet":"Feed Pres","index":2,"reason":"not_a_worksheet"},{"sheet":"Perm Con.","index":3,"reason":"not_a_worksheet"},{"sheet":"Salt Passage (Norm)","index":4,"reason":"not_a_worksheet"},{"sheet":"Perm Flow (Norm)","index":5,"reason":"not_a_worksheet"},{"sheet":"Differential Pres (Norm)","index":6,"reason":"not_a_worksheet"},{"sheet":"Water Trans. Coefficient","index":7,"reason":"not_a_worksheet"},{"sheet":"Salt Trans. Coefficient","index":8,"reason":"not_a_worksheet"}],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"Data","index":0,"n_rows":15,"n_cols":42,"rows_kept":15,"cut":false,"hidden":false,"merged":[[9,13,9,17],[9,18,9,38],[9,6,9,7],[9,8,9,9],[9,10,9,12]]}
[null,null,null,null,null,"System"]
[null,null,null,null,null,null,"Train",null,null,null,null,null,null,null,null,null,null,null,null,"Standard Test Conditions",null,null,null,null,"System",null,null,null,null,"Conversion Factors"]
[null,null,null,null,null,null,"Element Selection",null,null,null,null,null,null,null,null,null,null,null,"Perm Flux","EFX",null,null,"gfd",null,"Elements/Vessel",null,"EPV",null,null,"m3/h to gpm","gpmPERm3h",4.4028600000000004]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Area","EMAe",null,null,"sq ft",null,"Vessels",null,"V",null,null,"bar to psi","psiPERbar",14.5]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Perm Flow","Qpe",null,null,"GPD"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,"401 Jones Rd, Oceanside, CA 92054",null,null,null,"Constant","Ke",null,null,"no units",null,null,null,null,null,null,null,null,null,null,"401 Jones Rd, Oceanside, CA 92054"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,"1-800-901-2500",null,null,null,"Net Drive Pressure","NDPe",null,null,"PSI",null,null,null,null,null,null,null,null,null,null,"1-800-901-2500"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,"info@hydranautics.com",null,"www.membranes.com",null,"Concentration - feed","Cfe",null,null,"ppm",null,null,null,null,null,null,null,null,null,null,"info@hydranautics.com",null,"www.membranes.com"]
["Version 8"]
[null,null,null,null,null,null,"Concentration",null,"Flows",null,"Pressures",null,null,"Normalized Data",null,null,null,null,"Calculated Data"]
[null,null,null,null,null,null,"Feed","Permeate","Con",{"$f":"lblPerm","v":"Permeate"},{"$f":"G11","v":"Feed"},{"$f":"lblBrine","v":"Con"},{"$f":"lblPerm","v":"Permeate"},"Salt Passage","Permeate Flow","Differential Pres.","Water Transport Coefficient","Salt Transport Coefficient"]
["Date","Hour","Turbidity","SDI","pH","T","Cf","Cp","Qc","Qp","Pf","Pc","Pp","SSPn","QSPn","DPn","WTCn","STCn","Rec","DP","Day","To","Cfo","Cpo","Qco","Qpo","Pfo","Pco","Ppo","ConF","Cf ave","FOP ave","POP","DPo","NDP","SFX","SSP","SSR","TCF","ASPn","Operator"]
[null,null,"NTU",null,null,"C","ppm",{"$f":"SalinityUnits","v":"ppm"},"gpm",{"$f":"FlowUnits","v":"gpm"},"psi",{"$f":"PresUnits","v":"psi"},{"$f":"PresUnits","v":"psi"},"%",{"$f":"FlowUnits","v":"gpm"},{"$f":"PresUnits","v":"psi"},"m/s - kPa","m/s","%",{"$f":"PresUnits","v":"psi"},"days","C","ppm","ppm","gpm","gpm","psi","psi","psi","ppm","ppm","psi","psi","psi","psi","gfd","%","%","no units","%",null,"Comments"]
[]
["InsertRow"]

{"sheet":"Language","index":9,"n_rows":49,"n_cols":7,"rows_kept":49,"cut":false,"hidden":false,"merged":[]}
["When new language is added:"]
["1.  Update the dropdown box on the frmSetup with the  new language"]
["2.  Update the subroutine \"MainLabelSetup\""]
["3. Rename the column on line 10  where the new language is inserted"]
["4. Highlight column and change column definition"]
["Trains",1]
["First Time",true]
["LangUnits",0]
[null,0,1,2,3,4,5]
[null,"English","Spanish","Portuguese","Japanese(kanji)","中文","French"]
[null,"Project Name","Proyecto ","Nome do Projeto","プラント名","项目名称","Nom du Projet"]
[null,"Train","Banco","Banco","トレイン","列","Ligne"]
[null,"Date","Fecha","Data","日付","日期","Date"]
[null,"Hour","Hora","Hora","時間","时间","Heure"]
[null,"Feed pH","pH Alim.","pH Alim.","供給液 pH","给水pH","pH Alim."]
[null,"Feed Temp","Temp. Alim.","Temp. Alim.","供給液 温度","给水温度","Temp. Alim."]
[null,"Feed Salinity","Salinidad Alim.","Salinidade Alim.","供給液 塩濃度","给水含盐量","Salinité Alim."]
[null,"Perm Salinity","Salinidad Perm.","Salinidade Perm.","透過液 塩濃度","产水含盐量","Salinité Perm."]
[null,"Conc Flow","Flujo Conc.","Fluxo Concentrado","濃縮流量","浓水流量","Débit Concentrat"]
[null,"Permeate Flow","Flujo Permeado","Fluxo Permeado","透過液流量","产水流量","Débit Perméat"]
[null,"Feed Pressure","Presión Alim.","Pressão Alim.","供給圧力","给水压力","Pression Alim."]
[null,"Conc Pressure","Presión Conc.","Pressão Conc.","濃縮圧力","浓水压力","Pression Conc."]
[null,"Perm Back Pres","Contrapresión Perm.","Contrapressão Perm.","透過液 背圧","产水背压","Contre-pression Perm."]
[null,"Element Selection","Selección Elemento","Escolha da Membrana","エレメント選択","膜元件选择","Sélection de l'Elément"]
[null,"Elements / vessel","Elementos /tubo","Elementos / Vaso","ベッセル当りのエレメント本数","膜元件数量／每支压力容器","Eléments / Tube"]
[null,"Vessels","Tubos","Vasos","ベッセル","压力容器数量","Tubes Pression"]
[null,"Standard Test Conditions","Condiciones de Prueba Estándar","Condições de Teste","標準テスト条件","标准测试条件","Conditions standards de test "]
[null,"Area (sq. ft.)","Area (p²)","Área (ft 2)","膜面積 (ft 2)","膜面积(ft 2)","Surface (ft 2)"]
[null,"Feed TDS (ppm)","SDT Alim.","Alim. TDS (ppm)","供給液　TDS（ppm）","给水TDS(ppm)","TDS Aliim."]
[null,"Flow (gpd)","Flujo (gpd)","Fluxo (gpd)","流量(gpd)","流量(gpd)","Flux (gpd)"]
[null,"Rej (%)","Rechazo (%)","Rejeição","除去率(%)","脱盐率（％）","Rejection (%)"]
[null,"TCF","FCT","TCF","温度換算係数","温度校正系数","FCT"]
[null,"NDP (psi)","PNA (psi)","NDP (psi)","実効運転圧力 (psi)","净驱动压力(psi)","PEN (psi)"]
[null,"Operator","Operador","Operador","作業者","操作人","Opérateur"]
[null,"Comments","Observaciones","Comentários","コメント","评论","Commentaires"]
[null,"Add Data","Introduzca Datos","Adicionar Dados","入力データ","加入数据","Introduire les Données"]
[null,"Operation Data","Datos de Operación","Dados Operacionais","操作データ","运行数据","Données de Fonctionnement"]
[null,"Reference Data","Datos de Referencia","Dados de Referência","参照データ","参考数据","Données de Référence"]
[null,"Concentration","Concentración","Concentração","濃度","浓度","Concentration"]
[null,"Flows","Flujos","Fluxos","透過流量","流量","Débits"]
[null,"Pressures","Presiones","Pressões","圧力","压力","Pressions"]
[null,"Calculated Data","Datos Calculados","Dados Calculados","計算値","计算值","Données Calculées"]
[null,"Normalized Data","Datos Normalizados","Dados Normalizados","温度補正データ","标准化值","Données Normalisées"]
[null,"Feed","Alim","Alim.","供給","给水","Alim."]
[null,"% Salt Passage","Paso de Sales ","Passagem de Sal","塩透過度","透盐率","Passage de Sels"]
[null,"Permeate Flow","Flujo de Permeado","Fluxo de Permeado","透過液流量","产水流量","Débit Perméat"]
[null,"Differential Pressure","Diferencial de Presión","Diferencial de Pressão","差圧","压差","Pression Différentielle"]
[null,"Water Transport Coefficient","Coef. Transp. Agua","Coef. Transp. Água","水透過係数","水透过系数","Coéficient de Transport de l'Eau"]
[null,"Salt Transport Coefficient","Coef. Transp. Sal","Coef. Transp. Sal","塩透過係数","盐透过系数","Coéficient de Transport des Sels"]

{"sheet":"Data Collection Form","index":10,"n_rows":22,"n_cols":15,"rows_kept":22,"cut":false,"hidden":false,"merged":[[20,12,21,14],[20,11,21,11],[1,8,2,10],[1,11,2,11],[1,12,2,14],[3,10,3,11],[3,12,3,14],[1,0,2,0],[1,7,2,7],[3,0,5,0],[3,1,5,1],[3,2,5,2],[1,1,2,6],[20,0,20,1],[20,2,21,2],[3,4,3,6],[3,7,3,9],[20,7,21,7],[20,4,21,6],[20,8,21,10]]}
["Print and use this form for manual data collectoin.  Data from this form should be entered into ROdataXL"]
["Site:",null,null,null,null,null,null,"Train/ Skid:",null,null,null,"Stage:"]
[]
["Date","Time","Operator",null,"FEED",null,null,"CONCENTRATION",null,null,"FLOWS",null,"PRESSURES"]
[null,null,null,null,"SDI","pH ","Temp","Feed","Perm","Conc","Conc","Perm","Feed","Conc","Perm"]
[null,null,null,"UNITS:"]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
["COMMENTS:"]
["Date","Time"]

{"sheet":"Cleaning Chem Use","index":11,"n_rows":23,"n_cols":15,"rows_kept":23,"cut":false,"hidden":true,"merged":[[17,0,17,2],[11,0,11,1],[2,5,2,6],[2,12,2,13],[2,0,2,3],[2,8,2,9]]}
["Estimated Cleaning Chemical Consumption Calculations"]
[]
[null,null,null,null,"Solution 1","Solution 3",null,"Solution 1","Solution 3",null,"Misc","Solution 1","Solution 3",null,"Misc"]
[null,"Cleanings  per Year: Target","Cleanings per Year: Max","Estimated Stage Cleaning Hold Up Volume (Liters)","Citric Acid per stage per cleaning (kg/clean)","STP per stage per cleaning  (kg/year)","SDBS per stage per cleaning (kg/yr)","Target Citric Acid (kg/year)","Target STP (kg/year)","Target SDBS (kg/yr)","Target NaOH (kg/yr)","Max Citric Acid (kg/year)","Max STP (kg/year)","Max SDBS (kg/yr)","Max NaOH (kg/yr)"]
["Stage 1",2,4,{"$f":"B23*B22*B20*2+E20","v":67200},{"$f":"B13*D5","v":1409.604221635884},{"$f":"B14*D5","v":1365.2770448548813},{"$f":"B15*D5","v":171.98944591029021},{"$f":"$B5*E5","v":2819.2084432717679},2730.5540897097626,343.97889182058043,500,{"$f":"$C5*E5","v":5638.4168865435358},5461.1081794195252,687.95778364116086,700]
["Stage 2",3,6,{"$f":"B23*B22*B21*2+E21","v":33600},{"$f":"B13*D6","v":704.80211081794198},{"$f":"B14*D6","v":682.63852242744065},{"$f":"B15*D6","v":85.994722955145107},2114.4063324538261,2047.9155672823219,257.98416886543532,500,4228.8126649076521,4095.8311345646439,515.96833773087064,500]
["Train",null,null,null,null,null,null,{"$f":"SUM(H5:H6)","v":4933.614775725594},4778.4696569920843,601.96306068601575,1000,9867.2295514511879,9556.9393139841686,1203.9261213720315,1200]
["Plant",null,null,null,null,null,null,{"$f":"H7*$B$19","v":39468.918205804752},38227.757255936674,4815.704485488126,8000,78937.836411609504,76455.514511873349,9631.408970976252,9600]
["Plant + Safety",null,null,null,null,null,null,{"$f":"H8*1.1","v":43415.810026385232},42050.532981530348,5297.2749340369392,8800,86831.620052770464,84101.065963060697,10594.549868073878,10560]
["Est Chem Cost",null,null,null,null,null,null,{"$f":"H8*D13","v":40652.985751978893},{"$f":"I8*D14","v":24848.042216358841},{"$f":"J8*D15","v":11316.905540897096},{"$f":"K8*D16","v":3520},{"$f":"L8*D13","v":81305.971503957786},{"$f":"M8*D14","v":49696.084432717682},{"$f":"N8*D15","v":22633.811081794192},{"$f":"O8*D16","v":4224}]
[]
["Chemical Use Data"]
["Solution 1 Conc",{"$f":"7.95/379","v":2.0976253298153034E-2},"kg/L Citric Acid",1.03,"$/kg CA"]
["Solution 2 Conc",{"$f":"7.7/379","v":2.0316622691292877E-2},"kg/L STP",0.65,"$/kg STP"]
[null,{"$f":"0.97/379","v":2.5593667546174141E-3},"kg/L SDBS",2.35,"$/kg SDBS"]
[null,null,null,0.44,"$/kg NaOH"]
[]
["Estimated Hold-up Volume Data"]
["Total Trains =",8,null,"Cleaning Flow Rate Vessel = ",150,"L/min"]
["1st Stage Array =",84,null,"Cleaning Tank Volume =",{"$f":"3*E19*B20","v":37800},"Liters"]
["2nd Stage Array =",42,null,"Cleaning Tank Volume =",{"$f":"3*E19*B21","v":18900},"Liters"]
["Elements/Vessel =",7]
["Liters/Element = ",25]

{"sheet":"Cleaning Data","index":12,"n_rows":54,"n_cols":8,"rows_kept":54,"cut":false,"hidden":true,"merged":[[13,0,17,0],[13,3,17,3],[13,4,17,4],[13,5,17,5],[7,0,11,0],[7,3,11,3],[7,4,11,4],[7,5,11,5],[25,0,29,0],[25,3,29,3],[25,4,29,4],[25,5,29,5],[19,0,23,0],[19,3,23,3],[19,4,23,4],[19,5,23,5],[49,0,53,0],[49,3,53,3],[49,4,53,4],[49,5,53,5],[43,0,47,0],[43,3,47,3],[43,4,47,4],[43,5,47,5],[31,0,35,0],[31,3,35,3],[31,4,35,4],[31,5,35,5],[37,0,41,0],[37,3,41,3],[37,4,41,4],[37,5,41,5],[43,6,47,6],[1,1,1,3],[2,1,2,3],[49,6,53,6],[31,6,35,6],[37,6,41,6],[19,6,23,6],[25,6,29,6],[7,6,11,6],[13,6,17,6]]}
[null,"RO Cleaning Data"]
[null,"Periodic cleaning of the RO system may be necessary to remove foulants and restore membrane performance.  Cleaning information recorded in the table below may assist in determining the nature of the foulant and the effectiveness of the cleaning. "]
[null,"Additional information on determining fouling and cleaning of RO membranees may be found on the Hydranautics web site www.membranes.com"]
[]
[]
["Table A","Cleaning Data"]
["Cleaning Date","Chemicals","Concentrations","pH","Temp ( C )","Recirc Time (hours)","Soak Time (hours)","Comments"]
[null,1,1]
[null,2,2]
[null,3,3]
[null,4,4]
[null,5,5]
[]
[null,1,1]
[null,2,2]
[null,3,3]
[null,4,4]
[null,5,5]
[]
[null,1,1]
[null,2,2]
[null,3,3]
[null,4,4]
[null,5,5]
[]
[null,1,1]
[null,2,2]
[null,3,3]
[null,4,4]
[null,5,5]
[]
[null,1,1]
[null,2,2]
[null,3,3]
[null,4,4]
[null,5,5]
[]
[null,1,1]
[null,2,2]
[null,3,3]
[null,4,4]
[null,5,5]
[]
[null,1,1]
[null,2,2]
[null,3,3]
[null,4,4]
[null,5,5]
[]
[null,1,1]
[null,2,2]
[null,3,3]
[null,4,4]
[null,5,5]

{"sheet":"Additional Data","index":13,"n_rows":8,"n_cols":10,"rows_kept":8,"cut":false,"hidden":false,"merged":[[2,0,2,3],[3,0,3,3],[5,0,5,1]]}
[null,"Additional RO System Operational Data"]
[]
["In addition to the data needed to normalize the performance data (see Data sheet in this file) there are other critical data which need to be recorded and tracked.  It is important to track these  parameters; failure to do so may affect the long term success of the RO membranes."]
["A list of parameters is given below.  You can use this sheet to record the results.  "]
["TABLE B  Additional System Data"]
["Freqency",null,"Annually, or more frequently during salinity upsets.","Daily if oxidant is used anywhere in the process.  Otherwise Annually.","Daily if oxidant is used anywhere in the process.  Otherwise Annually."," Start-up, or during O&G upsets","Annually, or more frequently during TOC upsets","Contin- uously (record daily value)","When required","When required"]
["Date","Hour","Feed Water Analysis","Chlorine","Redox","O&G","TOC","Turbidity","Cartridge Filter Change","Cleaning Event"]
["mmddyy","hhmm",null,"mg/L","mV","mg/L","mg/L","NTU",null,"Hi/Lo/Other"]

{"sheet":"Element Info","index":14,"n_rows":111,"n_cols":9,"rows_kept":111,"cut":false,"hidden":false,"merged":[]}
[]
[]
[]
[]
[]
[]
["Element information must begin at row 10"]
["Element","Area","Feed Con","Flow","Rej","TCF","NDP","Diameter","Length"]
[null,"ft 2","TDS","GPD","%",null,"psi","in","in"]
["CPA2-4040",85,1500,2250,99.5,2700,206,4,40]
["CPA2",365,1500,10000,99.7,2700,206,8,40]
["CPA2-8540",445,1500,12000,99.5,2700,206,8.5,40]
["CPA3",400,1500,11000,99.6,2700,206,8,40]
["CPA3-LD",400,1500,11000,99.7,2700,206,8,40]
["CPA4",400,1500,6000,99.7,2700,206,8,40]
["CPA-4040E",65,1500,2250,99.5,2700,206,4,40]
["CPA5 -LD-4040",80,1500,2100,99.7,2700,206,4,40]
["CPA5-LD",400,1500,11000,99.7,2700,206,8,40]
["CPA5 MAX",440,1500,12000,99.7,2700,206,8,40]
["CPA6-LD",400,1500,8000,99.75,2700,206,8,40]
["LFC1-4040",85,1500,2300,99.4,2700,206,4,40]
["LFC1",400,1500,10000,99.5,2700,206,8,40]
["LFC2-4040",85,1500,2500,95,2700,206,4,40]
["LFC2",365,1500,11000,95,2700,206,8,40]
["LFC3-4040",85,1500,2000,99.6,2700,206,4,40]
["LFC3-LD-4040",80,1500,2100,99.7,2700,206,4,40]
["LFC3",400,1500,9500,88.6,2700,206,8,40]
["LFC3-LD",400,1500,11000,99.7,2700,206,8,40]
["ESPA-2514",5.0999999999999996,1500,250,99.4,2700,206,2.5,14]
["ESPA-2521",9.9,1500,350,99.4,2700,206,2.5,21]
["ESPA-2540",25.5,1500,750,99.4,2700,206,2.5,40]
["ESPA-4014",16.899999999999999,1500,500,99.4,2700,206,4,14]
["ESPA-4021",28.6,1500,1000,99.4,2700,206,4,21]
["ESPA-4611",31,1500,930,99.4,2700,206,4.5999999999999996,11]
["ESPA-4641",120,1500,3600,99.4,2700,206,4.5999999999999996,41]
["ESPA1-4040",85,1500,2600,99.3,2700,125,4,40]
["ESPA1",400,1500,12000,99,2700,125,8,40]
["ESPA2-4040",85,1500,1900,99.6,2700,125,4,40]
["ESPA2-LD-4040",80,1500,2000,99.6,2700,125,4,40]
["ESPA2",400,1500,9000,99.5,2700,125,8,40]
["ESPA2-LD",400,1500,10000,99.6,2700,125,8,40]
["ESPA2-31",400,1500,9000,99.6,2700,125,8,40]
["ESPA2 MAX",440,1500,12000,99.6,2700,125,8,40]
["ESPA2-1640",1600,1500,38000,99.6,2700,125,16,40]
["ESPA3-4040",85,1500,3000,98,2700,125,4,40]
["ESPA3",400,1500,14000,98.5,2700,125,8,40]
["ESPAB",400,1500,8600,99.2,2700,125,8,40]
["ESPAB MAX",440,1500,9000,99.3,2700,125,8,40]
["ESPAB-1640",1700,1500,34000,99.3,2700,125,16,40]
["ESPA4-4040",85,500,2500,99.2,2700,90,8,40]
["ESPA4",400,500,12000,99.2,2700,90,8,40]
["ESPA4-LD",400,500,12000,99.2,2700,90,8,40]
["ESPA4 MAX",440,500,13200,99.2,2700,90,8,40]
["ESNA1-4040",85,500,2300,80,2700,68,4,40]
["ESNA1",400,500,11000,80,2700,68,8,40]
["ESNA1-8540",445,500,12000,80,2700,68,8.5,40]
["ESNA1-LF",400,500,7400,86,2700,68,8,40]
["ESNA1-LF-LD",400,500,8200,89,2700,68,8,40]
["ESNA1-LF-4040",85,500,1600,86,2700,68,4,40]
["ESNA1-LF2",400,500,7800,80,2700,68,8,40]
["ESNA1-LF2-LD",400,500,10500,86,2700,68,8,40]
["ESNA1-LF2-4040",85,500,1700,80,2700,68,4,40]
["ESNA1-LF3",400,500,7200,88,2700,68,8,40]
["ESNA1-LF3-4040",85,500,1500,88,2700,68,4,40]
["HYDRACoRe50",365,500,8200,50,2700,68,8,40]
["HYDRACoRe50-4040",75,500,1700,50,2700,68,4,40]
["Nano-BW",400,2000,11000,99.7,2700,125,8,40]
["Nano-BW MAX",440,2000,12000,99.7,2700,125,8,40]
["Nano-SW",400,2000,11000,99.8,2700,413.5,8,40]
["Nano-SW MAX",440,2000,12000,99.8,2700,413.5,8,40]
["SANRO-HS-4",90,1500,2200,99.7,2700,206,4,40]
["SANRO-HS-8",380,1500,8800,99.7,2700,206,8,40]
["SANRO-HS2-4",90,1500,3000,99.6,2700,206,4,40]
["SANRO-HS2-8",380,1500,14000,99.6,2700,206,8,40]
["SWC-2514",5,32000,110,99.4,2700,413.5,2.5,14]
["SWC-2521",9.9,32000,220,99.4,2700,413.5,2.5,21]
["SWC-4014",16.8,32000,370,99.4,2700,413.5,4,14]
["SWC-4021",28.6,32000,640,99.4,2700,413.5,4,21]
["SWC1-4040",70,32000,1100,99.6,2700,413.5,4,40]
["SWC1",315,32000,5000,99.7,2700,413.5,8,40]
["SWC2-4040",70,32000,1400,99.2,2700,413.5,4,40]
["SWC2",315,32000,6200,99.2,2700,413.5,8,40]
["SWC3",370,32000,5900,99.7,2700,413.5,8,40]
["SWC4",370,32000,5500,99.8,2700,413.5,8,40]
["SWC4-LD",400,32000,6500,99.8,2700,413.5,8,40]
["SWC4 MAX",440,32000,7200,99.8,2700,413.5,8,40]
["SWC4-1640",1600,32000,36000,99.8,2700,413.5,16,40]
["SWC3+",400,32000,7000,99.8,2700,413.5,8,40]
["SWC4+",400,32000,6500,99.8,2700,413.5,8,40]
["SWC4B",400,32000,6500,99.8,2700,413.5,8,40]
["SWC4B-LD",400,32000,6500,99.8,2700,413.5,8,40]
["SWC4B MAX",440,32000,7200,99.8,2700,413.5,8,40]
["SWC5",400,32000,9000,99.8,2700,413.5,8,40]
["SWC5-4040",85,32000,1900,99.7,2700,413.5,4,40]
["SWC5-LD-4040",80,32000,1750,99.7,2700,413.5,4,40]
["SWC5 MAX",440,32000,9900,99.8,2700,413.5,8,40]
["SWC5-LD",400,32000,9000,99.8,2700,413.5,8,40]
["SWC5-1640",1600,32000,34000,99.8,2700,413.5,16,40]
["SWC6",400,32000,12000,99.8,2700,413.5,8,40]
["SWC6-4040",85,32000,2500,99.7,2700,413.5,4,40]
["SWC6-LD",400,32000,12000,99.8,2700,413.5,8,40]
["SWC6 MAX",440,32000,13200,99.8,2700,413.5,8,40]
["SWC-2540",25.5,32000,520,99.4,2700,413.5,2.5,40]
[]
[]
["Note: Leave the last row blank so the program knows where the element list ends."]
["2004-02-02","New ESNA1-LF flow = 7400 gpd, add ESNA1-LF2 8040, LFC1-4040=99.5%, LFC3 = 99.7% rej, ESPA1-4040 = 99.3% ESPA2-4040 = 99.6%,ESPA3 14000gpd and 99.3%"]
["2004-02-05","New ESNA1-LF2 and ESNA1-LF3"]
["2010-05-15","New elements added. + names changed to MAX"]
["2010-04-14","New elements added (SANRO-HS-4,SANRO-HS8, SANRO-HS2-4,SANROHS2-8,SWC4B MAX, SWC4-1640, SWC5-1640 and ESPA2-1640)"]
["2014-10-17","New elements added"]